## Slide 1: Profibus
Presenter: Abolfazl Daniali

## Slide 2: Befor PROFIBUS

## Slide 3: Problems
Extensive cabling due to direct wiring
Diagnostics are limited
Signals can be susceptible to unwanted noise interference

## Slide 4: PROFIBUS => Process fieldbus
Developed in 1989 by Siemens and PNO
Industrial communication protocol
Open standard
OSI Compliant
Used in Factory automation , Process automation , Drive technology , Hybrid application

## Slide 5: What is a fieldbus?
a field bus is a digital , serial , two-way , multi-drop communication link among controllers and its remote I/O, sensors ,acutators and inter-networking components

## Slide 6: Types of PROFIBUS
1.PROFIBUS DP (Decentralized Peripherals) 2.PROFIBUS PA (Process Automation)

## Slide 7: PROFIBUS DP
Two types of devices are supported
Master or active stations slave or passive stations
Control the bus receive messages
Send message without request Send message only on request

## Slide 8: PROFIBUS DP
Multiple masters are allowed
Each slave assigned only to one master:
  Multiple master can read from any device
  Only one master can write to any device

## Slide 9: PROFIBUS Communication
Two mechanism supported:
Token passing (master to master)
Polling
(master to slave)

## Slide 10: PROFIBUS Communication – token passing
During power up , lowest address master commences the initialization
and keeps the token with itself
When a master receives the token it can pass message to any slave or master
This software token is passed between the masters in ascending order, resulting in formation of a logical ring despite a bus topology.

## Slide 11: PROFIBUS Communication – polling
The Master initiates communication using Cyclic or Acyclic Messaging.
Slaves only respond when queried by the Master (they never initiate communication).

## Slide 12: Polling-cyclic
Used for real-time control, where the Master continuously polls Slaves.
Process:
  The Master sends a Cyclic Data Request.(request frame)
  The Slave processes the request and replies with data.(response frame)
  This process repeats at predefined intervals.
Example:
  A PLC (Master) repeatedly polls a sensor (Slave) for temperature values every 10ms.

## Slide 13: Polling-cyclic
Header and Trailer sections consists of information for addressing , error checking and other protocol related data.

## Slide 14: Polling-Acyclic
Used for non-time-critical data like diagnostics, configuration, and maintenance.
Process:
  The Master sends a special request (e.g., a configuration update).
  The Slave processes the request and responds only once.
  The normal cyclic process resumes.
Example:
  A DCS (Master) requests firmware information from a field device.

## Slide 15: Error Handling in PROFIBUS
Automatic Retransmissions: If a Slave fails to respond, the Master retries.
Timeouts: If multiple retries fail, the device is marked as faulty.
Checksum Validation: Ensures data integrity.

## Slide 16: Profibus DP and PA
PROFIBUS is mainly used for high-speed input/output devices and to link intelligent devices such as drives.
It can use different physical layers such as RS-485 (most common), wireless, or fiber optics.
PROFIBUS PA refers to the following additional features:
Bus powered by using the Manchester encoded Bus Powered (MBP) physical layer according to IEC 61158-2.
Intrinsically safe design.
Configuration over the bus.
Device profile.

## Slide 17: summary
Befor PROFIBUS
Fieldbus
Types of Profibus
PROFIBUS DP
PROFIBUS Communication
Error Handling in PROFIBUS
Comparing Profibus DP and PA

## Slide 18: resources
What is PROFIBUS and how it works?
Online course on us.profinet.com
Siemens: PROFIBUS network manual

## Slide 19: Thanks for your attention